SOP: 9.4.631 – Release of Large Feeder Wire

Department: Project Management / Field Leadership / Purchasing

Related SOPs:

9.2.020 – Procurement of Large Feeder Wire -

9.2.160 – Develop Procurement Plan -

9.4.055 – Procurement of Large Feeder Wire -

9.4.605 – Issue Purchase Orders -

9.4.620 – Manage Expediting -

9.4.625 – Manage Delivery Tracking -

9.4.630 – Manage Material Receiving -

9.4.660 – Manage Procurement Closeout

Purpose

Standardizes the process for verifying, releasing, and tracking large feeder wire after procurement to ensure accuracy, proper sequencing, and timely delivery.

Scope

Applies to all large feeder wire (1 AWG and larger) released from vendor storage for installation .

Roles & Responsibilities

Requirements

- Wire procured Approved submittals complete Conduit installed Feeder Wire Procurement & Release Log updated

Procedure

Step 1 – Field Measurement Include pulls in 3-week look-ahead. Confirm conduit is ready. Measure with true tape; use scaled drawings only if necessary. Document in Feeder Wire Procurement & Release Log: Source and destination Number of conductors Ground size/type Parallel runs (if applicable) Allowances (e.g.,  250’ tape + 10’ risers + 5’ makeup per end ) Indicate Delivery Date for JIT delivery. Record cut lengths in the  Feeder Release  tab. Step 2

Pull Sequencing When a single pull isn’t practical: Group runs by size/type. Define reel sharing and pull order. Example Pull Sequence Strategy:  Pull A = 300 ft Pull B = 50 ft Pull G = 250 ft  Recommended Put-Up: One 600-ft reel per conductor.  Pull Order: Pull A and G first, then B last.  Why:  If longer pulls are short, the short run (B) can absorb the variance, minimizing the impact if new wire is needed.  Step 3 PM Review Validate against estimate and specs (material, color, ground, etc.). Approve and submit release/PO to vendor. Step 4 Vendor Cut & Tag Cut/bundle per instructions. Tag reels by destination and bundle. Bundle phases and ground as specified. Schedule JIT delivery. Step 5 Jobsite Receipt Foreman verifies: Reels match plan Labels and lengths correct Wire undamaged Report discrepancies to PM within 24 hours. Step 6 Reel Return & Credits Track returned reels and unused wire. Log credits in Feeder Wire Workbook.

Appendix